## Slide 1: Peppermill Renewable Energy Program
Geothermal
One of the Greatest Renewable Energy’s Available
Review Peppermill’s Geothermal Story

## Slide 2: Peppermill Renewable Energy Program
5 Year Expansion
Property doubled in size
  60 Acre Resort
  2.2 Million Square Feet of Facility
  1,640 hotel rooms
  9 Restaurants
  200,000 sq. ft convention space
  3 swimming pools

## Slide 3: Peppermill Renewal Energy Program
Real Time Concerns
Second largest energy user in Reno.
Utility bills (gas, electricity & water) doubled
Economy slowed down – affecting revenue.
Started researching renewable energy alternatives.

## Slide 4: Peppermill Renewable Energy Program
Chart: 
| 2010 | 2012
Jan | 287 | 54
Feb | 249 | 52
Mar | 234 | 49
Apr | 228 | 38
May | 201
Therm $ Before Geothermal
Therm $ After
Geothermal
Natural Gas Consumption

## Slide 5: Peppermill Renewable Energy Program
Renewable Energy Alternatives
Reviewed energy resources available
Choosing best energy
Cost & expenses involved
Methods of obtaining the resource
Risks
Rate of return on investment

## Slide 6
Choosing Geothermal
  Shallow Well Operations since 1980’s
  Active geothermal reservoir underground
  Energy not utilized to it’s fullest capacity.
  Heated small outer building & pool.
Peppermill Renewable Energy Program

## Slide 7: Peppermill Renewable Energy Program
2008 Hotel Expansion
Completely over-hauled: Shallow Geothermal System
Installed new: - Stainless Steel Piping - Heat Exchangers - New Well Pumps - VFD drives - Water Holding Tanks - Front End Connections

## Slide 8: Peppermill Renewable Energy Program
Production Well #2
  Drilled early 1980
  Casing - 6”
  Depth - 934’
  Temp - 128 deg
  GPM - 175
  25HP Hayes 6 - stage pump
  Pump depth – 200’

## Slide 9: Peppermill Renewable Energy Program
Shallow Well – Heated:
  600 Suite Hotel – Domestic water
  Two main swimming pools
  Two Jacuzzi pools
Reduces Central Plant NG Boiler heat load by 30%
1.5 Year pay back

## Slide 10: Peppermill Renewable Energy Program
Expansion Tanks
  Stores domestic water heated by Geothermal
  Heats Tuscan Tower domestic hot water
    12 – 1,000 gallon holding tanks
    127 degree water
    Supplies hot water to showers & bathrooms

## Slide 11: Peppermill Renewable Energy Program
New Production Well - #8
  Ensign Drilling Co.
  28 days to drill
  24/7 Operation
  South Central Plant Lot
  Sound Barrier Walls - Noise concerns - Neighbors

## Slide 12: Peppermill Renewable Energy Program
New Production Well - #8
  4,421’ Vertical
  9 5/8” Well Casing
  Flows Artesian @ 38 psig
  Produces 1,500 GPM
  174 degree fluids
  Provides 100% campus heat load

## Slide 13: Peppermill Renewable Energy Program
Trenching Operations
PW #8 to IW #9 piping
1,500’ of new 10” piping
Schedule 80, black steel, seamless – 1,070 p.s.i.g
Communication and power
Traffic control, noise, storm drain protection.

## Slide 14: Peppermill Renewable Energy Program
Reinjection Piping
  Engineering Challenges
  Pipe fabricated through Hotel Tower corridor’s
  Connects Production Well #8 to Injection Well #9

## Slide 15: Peppermill Renewable Energy Program
New Reinjection Well #9
  IW #9 – Drilled in January 2010
  Ensign Drilling Derrick – 127 feet high
  Geothermal Fluid flow test
  Baker Hughes Tanks

## Slide 16: Peppermill Renewable Energy Program
Injection Well #9
Vertical Bore Hole Schematic
  30” Ground level casing
  9.6” Casing at the bottom
  Well is 3,900’ deep
  Handle 1,500 GPM

## Slide 17: Peppermill Renewable Energy Program
Baker Hughes Injection Pump
Horizontal skid layout
4 – stage 1,000 series pump
400 Hp Tyco Motor
Pumps geothermal fluids back into aquifer
600 p.s.i.g

## Slide 18: Peppermill Renewable Energy Program
PW #8 – Drive Gear
Central Plant
  Baker Hughes
  Centrilitf Pump
  Centrilitf VFD
  480 Volt – 3 phase transformer
6 stage production pump
  2,000 gpm rated
  Submersible
  Draw down @ 400’

## Slide 19: Peppermill Renewable Energy Program
Central Plant Boilers
  Cleaver Brook Boilers
  25,000,000 BTU’s each
    100,000,000 BTU’s total
    Natural Gas driven
  600 HP Boilers
  Annual Consumption
    2,400,000 Therms
    $2,200,000 NG Cost
    Reduce Carbon Footprint by 10,000 pounds.

## Slide 20: Peppermill Renewable Energy Program
Alfa Laval Heat Exchanger
  Plate & Frame
  1,500 GPM Rated
  Stainless channel plated @ 0.50 mm
  Rated 225 degrees
  Handles 150 p.s.i.g
  Temp meters – Weiss
  Flow meters - McCrometers

## Slide 21: Peppermill Renewable Energy Program
Geothermal Front End – Automating
  Invensys Software
  Geothermal graphic display
  Provides Valuable system Information
  Real Time
  Facility Wide Access

## Slide 22
Chart: 
| 2010 | 2011 | 2012
Jan | 287581 | 154590 | 89057
Feb | 249426 | 116957 | 77208
Mar | 234404 | 173047 | 82874
Apr | 222174 | 84290 | 63839
May | 200778 | 62162
June | 158379 | 62515
July | 85926 | 62706
August | 62356 | 54596
September | 61479 | 56188
October | 62840 | 59242
November | 72420 | 58420
December | 80013 | 73587
Peppermill Renewable Energy Program
3 Year NG History Chart
K
Started Geothermal July 2010

## Slide 23: Peppermill Renewable Energy Program
Future Vision
  Geothermal Electrical Generation
    4 - 6 mega watts
  Alternative Methods
    Geothermal power plant
    Binary - Turbine
  Fuel Cells – not good ROI

## Slide 24: Peppermill Renewable Energy Program
Artificial Grass Turf
  Annual Water Savings
    Replaced 40,000 sq. ft. of grass.
    Removed 120 – 3GPM sprinkler heads
    Rate: $1.72 / 1,000GPM
    5,184,000 Gallons of water savings per season
    $15,000 Annual Savings – Labor & Water use.

## Slide 25: Peppermill Renewable Energy Program
Electric Cars
  Fossil Fuel Savings
    Engineering & Security uses Electric cars
    Goes 8 hours on one charge
    Plugs into 110 Receptacle
    30 – 35 mph

## Slide 26: Peppermill Renewable Energy Program
Laundry Grey water recycling
  Aqua Recycling
    Installed 2008
    Capture Grey Wash Water
    Recycled the grey water
    Installation Cost $185,000
  2010 Operational Saving Facts
    Chemical Savings - $123,613
    Water/Sewer Savings - $122,141
    Annual Savings - $245,754
    ROI - 7 1/2 months
  3 - Year Savings Total - $737,264

## Slide 27: Peppermill Renewable Energy Program
Parking Lot Light Feasibility
  Existing Lights
    300 Metal Halide Lights
    1,000 watts each
    $103,680 Yr Electricity
  LED Light Replacement
    250 Watt with 50,000 hr life
    Unit Cost - $600 per unit
    Total LED Cost - $180,000
    $25,920 Yr Electricity
  ROI
    $ 41,250 - NV Energy Rebate
    $77,760 - Annual Electrical Savings
    1.7 Month - Payback
    $886,464 - Lifetime Savings